## MV_BOM_Tender_Sheet_AL300
Category | BOM Item | Quantity | Notes
Materials | CTP6 MV Junction Box A (STS05) | 1 Each | SS316/SS304 C5M, IP67/IK10, filtered breather, Cu earth bar; 1000x800x400 mm; gland plate sized to larger OD (see glands)
Materials | CTP6 MV Junction Box B (STS06) | 1 Each | SS316/SS304 C5M, IP67/IK10, filtered breather, Cu earth bar; 1000x800x400 mm; gland plate sized to larger OD (see glands)
Materials | CTP5 MV Junction Box (STS04) | 1 Each | SS316/SS304 C5M, IP67/IK10, filtered breather, Cu earth bar; 1000x800x400 mm; gland plate sized to larger OD (see glands)
Materials | Cable Drum Assemblies (Steel Reels) | 3 Each | Geometry scales with cable OD: barrel ≥ 18×OD; flange ≥ barrel + 6×OD; width per ordered length; AL300 OD typically ~73–80 mm
Materials | MV XLPE Cable (11 kV) | 1200 M | IEC 60502-2; 3C 300 mm² Aluminum; armored/sheath per route; provisional total (split per feeder after survey)
Materials | MV Termination Kits (12/20 kV) | 12 Set | Stress-control heat/cold-shrink; include Al/bimetal lugs/boots sized for 300 mm²; indoor @ switchboard; outdoor @ JB as required
Materials | Double-Compression Cable Glands (M90 class) | 18 Each | IP67; thread size to suit OD ~73–80 mm; check vendor datasheet; maintain armor continuity
Materials | Armor/Braid Bonding Kits | 6 Each | If required by selected cable type
Materials | Al/Bimetal Lugs (300 mm²) | 36 Each | Crimp or shear-bolt per dielist; sized to 300 mm² Al
Materials | Cu Earth Conductor (25–35 mm²) | 60 M | Bond JBs to earth grid; include slack
Materials | Cu Earth Bar with Test Link | 3 Each | Included in JB; spare allowed
Materials | Filtered Breathers | 6 Each | Two per JB
Materials | Neoprene Gaskets/Seals | 3 Set | Door and gland plate spares
Materials | Blanking Plugs | 24 Each | IP-rated for unused entries
Materials | Surge Protection (MV pit) | 3 Each | MOV/surge diverter suitable for 11 kV (if required by design)
Materials | Fasteners & Fixings (A4-80 SS) | 6 Set | Bolts, washers, isolating washers; mounting + spares
Materials | Mounting Backplates/Frames (SS316) | 3 Each | For JB mounting
Materials | Cable Support Saddles | 12 Each | Strain relief within 150 mm of entry
Materials | Cable Route Markers | 30 Each | UV-stable route tags/plates at pit entries and intervals
Materials | Labels & Plates | 3 Set | Engraved phenolic labels (JB IDs, feeder IDs)
Materials | Phase ID Sleeves | 6 Set | Heat-shrink phase markers (L1/L2/L3/PE)
Materials | Desiccant Packs | 12 Each | Moisture control packs
Materials | Sealants/Compounds | 6 Cartridge | IP-rated sealing compound for entries
Materials | Cable Lubricant | 6 Bottle | Approved pulling lubricant
Materials | Mechanical Protection at Pit Exits | 6 Set | Grommets/bushings/rub blocks
Materials | Portable Earths (rated) | 2 Set | Isolation safety during works
Materials | Padlocks & LOTO Hasps | 2 Set | For LOTO kits
Materials | Warning Signage | 3 Set | Electrical hazard and identification
Tools | Hydraulic Crimper + Die Set | 1 Each | 12–400 mm² range; calibrated; with dielist
Tools | Heat Gun/Heat Blower | 2 Each | Industrial grade with temperature control
Tools | Torque Wrench Set | 2 Set | 5–200 Nm with calibration; per torque log
Tools | Capstan Winch | 1 Each | Controlled speed for cable pulls
Tools | Inline Dynamometer | 1 Each | 0–5 kN tension measurement; record pulling tension
Tools | Spindle Stands/Drum Jacks | 2 Pair | Rated for drum mass; with brake; two drums concurrently
Tools | Cable Rollers & Corner Blocks (MV duty) | 2 Set | Pulling route control
Tools | Megger (5 kV IR Tester) | 1 Each | Insulation resistance testing
Tools | VLF Test Set (0.1 Hz | 12/20 kV class) | 1 Each | Withstand testing @ 2×U0
Tools | Earth Tester | 1 Each | Clamp or 3-point method instrument
Tools | Secondary Injection Test Set | 1 Each | Protection relay testing
Tools | Thermal Camera (≥320x240) | 1 Each | Post-energization thermal scan
Tools | Confined Space Gas Detector (4-gas) | 1 Each | For pit entry safety
Tools | LOTO Kit | 2 Set | Hasps, tags, locks, testers
Tools | Lifting Slings/Spreader | 2 Set | Rated slings and spreader bar
Tools | Hand Tools Set (insulated) | 2 Set | Cutters, strippers, spanners